## Kisii Package A (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 1: REHABILITATION AND EXTENSION PIPELINES IN KISII TOWN WATER PROJECT PACKAGE A
Construction and Rehabilitation of Water Distribution Pipelines (OD 50 - OD90; Total Length 4.2km) and Supply of 500Nr Cold Water Meters
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
CLASS A: GENERAL ITEMS
A 2.1 | General Information and requirements
Specific conditions in execution of these Works are deemed to be included in the Contractor's rates. The Contractor will be required to submit Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include but are not limited to the following: i. No blasting will be permitted in these areas ii. The Contactor to maintain uninterrupted continuity of water supply in existing mains iii. Pedestrian and vehicular Access to individual shops / plots to be maintained at all times iv. Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v. Allow for method related costs for laying water mains across existing active lines with minimal disruption of flow vi. Allow for method related costs for dewatering of trenches.
A 2.2 | Cost relating to the above mentioned specific conditions
Allow for method related charges the tenderer feels may be required. These should be idicated below with pricing for each item
A 2.2.1 | i) | Item | LS
A 2.3 | Survey Works
A 2.3.1 | Allow for Engineering Survey of the Proposed pipeline alignments including preparation of plan and profile with levels at 20m intervals horizontally | m | 4200
ESHS | Environmental, Social, Health and Safety (ESHS) Cost
ESHS 1 | Allow for any costs associated with compliance with environmental, health, and safety requirements in line with the Environmental and Social Management Plan (ESMP) provided for under Section IV of the technical specifications in the bid document. This compliance shall be consistent with the requirements of respective government agencies and prevailing legislation. The cost under this item shall include a quarterly environmental audit in the ESMP by a registered Lead Expert. | Item | PC
A260 | Testing of works
A260.1 | Pipeline testing and commissioning of the Pipeline (Outer Diameter varying from 50-90mm ) including provision of all equipment, materials and works necessary for testing such as but not limited to thrust bloks, anchor blocks,provision, transportation and use of water, pipe fittings,disposal of used water. | m | 4500
A260.2 | Disinfection of Pipeline (Outer Diameter varying from 50-90mm) : flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disifecting water | m | 4500
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS D: DEMOLITION AND SITE CLEARANCE
D1 | General siteclearance along the pipeline allignment. | ha | 1
D2 | Tree Cutting (Provisional)
Cut down trees, grub up roots and cart away to tips
D2.1 | Girth: 1.0 m - 2 m | Nr | 10
Note:- Girth shall be measured 1.0m above ground level
D2.2 | Demolish existing concrete plinths along pipeline alignment and hand over material to the owner. | m2 | 50
D2.3 | Demolish existing temporary structures along pipeline allignment and hand over materials to the owner (Approximate area 10m²) | Nr | 20
CLASS I: PIPE WORK - PIPES
Supply, Transport to Site and Store
I7 | High Density Polyethylene Pipes (HDPE)
I71.1 | Nominal bore 50mm | m | 1800
I71.2 | Nominal bore 63mm | m | 1500
I71.3 | Nominal bore 75mm | m | 1200
Transport from Site Store, Lay and Joint Pipes in Trench, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation trenches, Backfilling and final Reinstatement.
I7 | High Density Polyethylene Pipes (HDPE)
Nominal Bore 50 to 160mm in trenches
I712.1 | Depth not exceeding 1.5 m | m | 4500
CLASS J: PIPE WORK - FITTINGS AND VALVES - PN16
A | Supply, Transport to Site and Store
A-J3 | HDPE Pipe Fittings
A-J32 | Junction and Branches
HDPE Plain Ended TEE
A-J321.1 | OD 90 x OD 75 | Nr | 3
A-J321.2 | OD 75 x OD 63 | Nr | 3
A-J321.3 | OD 50 x OD 50 | Nr | 2
A-J321.4 | OD 50 x OD 40 | Nr | 3
A-J33 | Tapers
Plain Ended Concentric Taper
A-J331.1 | OD 63 x OD 50 | Nr | 2
A-J331.2 | OD 50 x OD 40 | Nr | 2
A-J331.3 | OD 40 x OD 32 | Nr | 2
A-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
A-J341.1 | OD 63 | Nr | 2
A-J341.2 | OD 50 | Nr | 2
A-J341.3 | OD 40 | Nr | 4
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A-J35 | Plain Ended Saddle Clamps
A-J351.1 | OD 63 x OD 50 | Nr | 2
A-J351.2 | OD 50 x OD 40 | Nr | 2
A-J351.3 | OD 40 x OD 32 | Nr | 2
A-J36 | Plain Ended Blank Flange
A-J361.1 | OD 63 | Nr | 2
A-J361.2 | OD 50 | Nr | 2
A-J361.3 | OD 40 | Nr | 3
A-J361.4 | OD 32 | Nr | 3
A-J37 | Valves and Penstocks
A-J371 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
A-J371.2 | DN 75mm | Nr | 5
A-J371.3 | DN 63mm | Nr | 2
A-J371.4 | DN 50mm | Nr | 2
A-J38 | Air Valve
A-J381 | Single Orifice Air Valve
A-J381.1 | DN 50 | Nr | 5
CLASS J: PIPE WORK - FITTINGS AND VALVES
B | Transport from Site Store, Install and fix all the fittings in treches and chambers.
B-J3 | HDPE Pipe Fittings
B-J32 | Junction and Branches
HDPE Plain Ended TEE
B-J321.1 | OD 90 x OD 75 | Nr | 3
B-J321.2 | OD 75 x OD 63 | Nr | 3
B-J321.3 | OD 50 x OD 50 | Nr | 2
B-J321.4 | OD 50 x OD 40 | Nr | 3
B-J33 | Tapers
Plain Ended Concentric Taper
B-J331.1 | OD 63 x OD 50 | Nr | 2
B-J331.2 | OD 50 x OD 40 | Nr | 2
B-J331.3 | OD 40 x OD 32 | Nr | 2
B-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
B-J341.1 | OD 63 | Nr | 2
B-J341.2 | OD 50 | Nr | 2
B-J341.3 | OD 40 | Nr | 4
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
B-J35 | Plain Ended Saddle Clamps
B-J351.1 | OD 63 x OD 50 | Nr | 2
B-J351.2 | OD 50 x OD 40 | Nr | 2
B-J351.3 | OD 40 x OD 32 | Nr | 2
B-J36 | Plain Ended Blank Flange
B-J361.1 | OD 63 | Nr | 2
B-J361.2 | OD 50 | Nr | 2
B-J361.3 | OD 40 | Nr | 3
B-J361.4 | OD 32 | Nr | 3
B-J38 | Valves and Penstocks
B-J381 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
B-J81.1 | DN 75mm | Nr | 5
B-J81.2 | DN 63mm | Nr | 2
B-J81.3 | DN 50mm | Nr | 2
B-J38 | Air Valve
B-J381 | Single Orifice Air Valve
B-J381.1 | DN 50 | Nr | 5
CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, Reinforcement, Formwork, Joints and Finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
K11 | IN SITU MASONRY CHAMBERS
K12 | Depth not exceeding 1.5m
K212.1 | Provide all materials and construct masonry walling for GATE/AIR VALVE Chambers on Reinforced Concrete Base, internal dimensions 1200mm x 1200mm. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc; | Nr | 4
K6 | Crossings
K652 | Allow for crossing existing drains and reinstatement after completion of the construction works. Include for provision of a divertion and keeping it operational during construction. | m | 50
K662 | Allow for crossing existing underground services(water lines, sewerlines, telephone/electricity ducts, fibre optic cableduct etc.) including reistatement to the original status and liason with the relevant body for inspection/approval during execution of the works. Pilot excavation shall be done to establish exact location of any buried services prior to actual excavation. The rate shall be demeed to include for pilot excavations, repairs and reistatement of any damages to the existing buried services as a result of execution of the works. | Item | LS
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K7 | Relocation / Reinstatement
K732.1 | Breaking up, Temporary and Permanent Reinstatement of MURRAM road with 300mm thick well graded stabilised gravel with 3% cement content base compacted in layers of 150mm thick using an 8-10 tonne roller. Contractor to allow for provision of requisite diversion signage, controls and safety precaution in his rates | m | 100
K732.2 | Breaking up temporary and permanent reinstatement of paved footpaths (concrete, cabro, tarmac, etc.). Pipe bore not exceeding 150mm | m | 100
K8 | Other Pipework Ancillaries
K82 | Excavate for, supply and fix concrete Marker Posts along the the water main route, road crossings, change of direction, air valves, washouts and valve chambers at locations shown by the Engineer. All in accordance with details given in the standard drawings. | Nr | 35
CLASS L:- PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
L1 | Extras over excavation and backfilling for excavation in Rock. Rate to include carting away and disposal. (Provisional)
L11 | In pipe trench and chambers
L111.1 | Excavation in trench for rock class "A" | m³ | 400
L111.4 | Provide for reinstament of Paved areas to original Status | m | 200
Note:- Blasting is NOT permitted for Item L11
L7 | Concrete Support, Thrust Blocks, Stools and Anchor Blocks
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc
Class 20/20 Mass Concrete Thrust Blocks
NOTE:- The work includes pipe and fitting fixing
L71 | Volume:- Not exceeding 0.1 m³
L711 | To pipes nominal bore: 110mm | Nr | 20
New Connections
| Allow a Provisional Sum of Kshs 250,000 for transfer of existing connections from existing pipelines to new pipelines and new connections. Include for saddle clamps, stop cocks, control valves, etc | Item | PS |  | 250000
M | WATER METERS
Supply and deliver cold water meters according to the engineers' specification. All meters shall require pre- supply approval.
M.1 | Flanged Volumetric Water Meters
M.1.1 | DN50 | Nr | 10
M.1.2 | DN90 | Nr | 10
M.1.3 | DN100 | Nr | 10
M.2 | Cold Consumer Water Meters
M.2.1 | DN15 | Nr | 300
M.2.2 | DN20 | Nr | 100
M.2.3 | DN25 | Nr | 50
M.2.4 | DN 40 | Nr | 10
M.2.5 | DN 50 | Nr | 10
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Kisii Package A (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 1: REHABILITATION AND EXTENSION PIPELINES IN KISII TOWN WATER PROJECT PACKAGE A
Construction and Rehabilitation of Water Distribution Pipelines (OD 50 - OD90; Total Length 4.5km) and Supply of 500Nr Cold Water Meters
Amount
(Kshs)
Page Total, Page 1 of 5
Page Total, Page 2 of 5
Page Total, Page 3 of 5
Page Total, Page 4 of 5
Page Total, Page 5 of 5
Bill No. 1.1 Total (Exclusive of Value Added Tax - VAT) carried to Grand Summary Sheet

## Kisii Package A - Grand Summary (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 1: REHABILITATION AND EXTENSION PIPELINES IN KISII TOWN WATER PROJECT PACKAGE A
GRAND SUMMARY
Bill | BILL DESCRIPTION | AMOUNT
Pacakge 1 | REHABILITATION AND EXTENSION PIPELINES IN KISII TOWN WATER PROJECT PACKAGE A
Construction and Rehabilitation of Water Distribution Pipelines (OD 50 - OD90; Total Length 4.5km) and Supply of 500Nr Cold Water Meters
Package 1 Total (A)
Sub-Total [Excl. VAT]; (A)
Add 5% Contingencies (B)
Total [Excl. VAT]; (C = A+B)
Add 16% VAT (D = 16% of C)
Grand Total [Incl. 16% VAT]; (E = C+D)

## Kisii Package B
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No. Tender No. Tender No. GWASCO/ CLSG II/KISII/2/2025/A_____
PACKAGE 2: EXTENSION OF PIPELINES AND ASSOCIATED WORKS FOR KISII TOWN WATER PROJECT PACKAGE B
Construction of Water Distribution Pipeline (OD 75; Total Length 2.6km), Rehabilitation of Existing 250m3 Masonary Tank and Construction of a Solar Booster Station at Milimani Tanks Site
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | PRELIMINARIES AND GENERAL ITEMS
1.1 | Provide provisional sum of Ksh. 50,000 for Capacity Building of pump operators on solar pump operations | Item | PS |  | 50000
1.2 | Provide a provisional sum of Ksh. 100,000 for Topographic Survey, wayleaves and approvals | Item | PS |  | 100000
1.3 | Provide a provisional sum of Ksh. 80,000 for Pipeline Pressure Testing and Disnifection | Item | PS |  | 80000
1.4 | Fabricate and install publicity boards clearly indicating the details of the project as directed by the engineer; | Nr | 2
1.5 | Provide a provisional sum of Ksh. 100,000 for Branding as directed by the Engineer | Item | PS |  | 100000
ESHS | Environmental, Social, Health and Safety (ESHS) Cost
ESHS 1 | Allow for any costs associated with compliance with environmental, health, and safety requirements in line with the Environmental and Social Management Plan (ESMP) provided for under Section II of the technical specifications in the bid document. This compliance shall be consistent with the requirements of respective government agencies and prevailing legislation. The cost under this item shall include a quarterly environmental audit in the ESMP by a registered Lead Expert. | Item | PC
2 | PUMP HOUSE
Substructure
2.1 | Clear the site of all bush shrub undergrowth and small trees grub up roots and cart away or burn all arising. | m2 | 15
Excavations and earthworks
2.2 | Remove top soil 150mm deep and heap soil on site as directed by the Engineer. | m2 | 8
2.3 | Excavate for strip foundation trenches not exceeding 1.50metres deep commencing from reduced level. | m³ | 8
2.4 | Allow for keeping excavations free from mud and all water including running water. | Nr | 1
2.5 | Load surplus excavated material and cart away. | m³ | 3
Hardcore
2.6 | Supply and hand pack imported hardcore fill including leveling and consolidating in 150mm layers. | m³ | 8
Blinding
2.7 | 50mm thick quarry dust blinding to the surface of hardcore; rolled smooth to receive 500g polythene sheet. | m2 | 15
Insecticide treatment
2.8 | 'TERMIDOL'' or other equal and approved chemical insecticide treatment prepared and applied according to the manufacturer's printed instructions. | m2 | 20
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
1000 Gauge polythene;150mm laps; measured overall
2.9 | Horizontal; 200mm wide. | m | 10
2.1 | 50mm thick blinding under strip foundations | m2 | 6
2.11 | Strip foundations 200mm Thick | m³ | 1
2.12 | 100mm thick ground floor slab | m³ | 1
Sawn formwork as described to:
2.13 | Edge of ground floor slab 150mm high | m | 10
Foundation walling in approved natural stones and jointed in cement and sand (1:3) mortar and reinforced with and including 20swg x 25mm wide hoop iron as described in;
2.14 | 200mm thick walls | m2 | 6
Superstructure.
Reinforced concrete (1:2:4/20-20mm aggregate) as described in Ring beams:
2.15 | Concrete | m³ | 0.4
High yield square twisted bars reinforcements including binding wire;
2.16 | D8 | kg | 13
2.17 | D12 | kg | 32
Sawn timber formwork to:
2.18 | Ring beams. | m2 | 4
Walling.
External Walling.
Load Bearing Walls. Hand dressed natural stone walling bedded and jointed in cement and sand (1:3) mortar and reinforced with and including 20swg x 25mm wide hoop iron as described in;
2.19 | 200 mm thick walling. | m2 | 21
Horizontal damp proof course ; one layer of 3 – ply bituminous felt or other equal and approved
2.2 | 200mm wide leveled and bedded in cement and sand (1:3) mortar under walls | m | 10
Roofing
Vibrated reinforced concrete (1:2:4/20-20mm aggregate) as described in:
2.21 | 150mm thick roof slab | m³ | 1
High yield ribbed bar reinforcements including binding wire.
2.22 | D12 | kg | 55
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Sawn formwork as described in:
2.23 | Soffits | m2 | 6
Steel windows with panels, handles, stays and hinges; permanent vents along full lengths of top edge; fixed with lugs built into concrete or block work;
2.24 | Window size 1250x1000mm overall; Ditto. | Nr | 1
Prepare and touch up primer and one undercoat and two finishing coats of gloss paint as "Crown" or other equal and approved; on metal surfaces.
2.25 | Windows (measured on both sides) | m2 | 3
Steel door complete with frame, ironmongery and glazing
2.26 | Single door size 1000x2100mm high. | Nr | 1
Internal & External Finishes.
Floor Finishes.
2.27 | 38mm thick cement sand screed 1:4 steel troweled | m2 | 6
Wall Finishes(Internal & External)
2.28 | 15mm lime plaster on concrete and block work to walls | m2 | 42
Painting & Decorating
2.29 | Prepare and apply three coats of silk emulsion paint to plastered walls as directed by the engineer | m2 | 142
3 | SOLAR PUMP INSTALLATION
Provide, Install, Test and Commission the following solar powered system
Subject to clause 13.2 of the G.C.C the contractor will be allowed to make proposals on the redesign of this Bill Item. All proposals from the contractor shall not lower the standard set herein by the Engineer.
Pump Unit
3.1 | Approved surface pump set of capacity 30m³/hr against a total head of 150m c/w all fitting, 21kw motor, current 31 A, mounting, and accessories | Nr | 1
Renewable Solar Inverter with build in Pump Controller
3.2 | Approved Hybrid Renewable Solar Inverter Solar with build in pump Controller with a Combined Control and Monitoring Unit. Incorporating a dry running protection, overload and over temperature protection, with integrated MPPT (Maximum Power Point tracker). should also allow for remote control, data logging and protection against reverse polarity. (equivalent svb/4t or SV 3 5.5 189) with a transferable warranty of a minimum 5 Years. | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
PV Module
3.3 | Approved 290 Watts, 24VDC Mono Crystalline PV Module to be connected in series to give minimum of solar array power c/w Wire kit array to control box, Wire kit array to array, Control Box, Copper Earth Cables 6mm, Earth rod c/w clamp and Lightning Arrestor. | Nr | 98
3.4 | Design as per radiations day angle, fabrication and installation of solar support structure for the specified solar panels. Rate to include for system testing. Use H-beams (single profile) cross section 150x150mm with 75mmx75mmx6mm struts and ties angle sections support to 38mmx6mm flat bars to hold panels tight into position. All joints braced. Height of the structure 5m above ground. The structure design must be preapproved before installation | Nr | 1
3.5 | PV disconnect switch 1000V/63A- 40-5 (Grundfos/Lorentz ) or equivalent | Nr | 1
3.6 | PV protect 1000-125 | Nr | 1
3.7 | Surge protector | Nr | 1
3.8 | 6mmx4 Core armoured Underground Cable | m | 25
3.9 | Armoured cable 10mm² 4 core underground cable for main load | m | 25
3.10 | Earth Rod C/W Clamp | Nr | 1
3.11 | Copper Earth Cable 25mm | m | 25
3.12 | Solar security light (300W Solar Module with in-built battery, Dawn-to dusk controller, 6m high pole) | Nr | 4
3.13 | Lightning arrester | Nr | 1
3.14 | Provisional sum of Ksh 50,000 for installation sundries Including interwiring cable (Provisional) | Item | PS |  | 50000
3.15 | DN 50 mm water meter c/w flanges and reed switch | Nr | 1
3.16 | 22 kW sunverter | Nr | 1
4 | ELECTRIFICATION OF PUMP HOUSE
4.1 | Provide a prime cost sum of KES 150,000 for Application and power connection to the Nearest KPLC grid and electrify pump house | Item | PC |  | 150000
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
5 | REHABILITATION OF EXISTING 300m3 MASONARY TANK
Allow for rehabilitation, testing and commissioning of the existing Masonry tank at Kiamabundu secondary.
Internal and External Plaster
5.1 | Hack the existing internal Plaster , clean and cart away the debris to the satsfaction of the Engineer | m2 | 98
5.2 | Provide 15 mm waterproofed mortar inclusive with a water bar as per the specification for internal plaster ratio 1:3 | m2 | 98
5.3 | Prepare and apply a cement mortar plaster on the external walls | m2 | 128
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Connections
5.4 | Fix steel lockable manhole covers | Nr | 6
6 | WATER TRANSMISSION PIPELINE
Rising Main
6.1 | Supply, store and lay HDPE Pipes 75mm PN 20 | m | 2600
Distribution Line
6.2 | Allow for provisional sum of KES 500,000 for assorted fittings to include interconnection from the the tank to the existing network as directed by the engineer | Item | PS |  | 500000
In pipe trench and chambers
6.3 | Excavate in soft materialand lay(trench should be at least 0.6m deep), Pipelaying and Backfilling | m | 2400
6.4 | Excavation in trench for rock class "A" | m | 200
6.5 | Allow for micro Tunnelling on a paved road as directed by the engineer | m | 15
6.6 | Provide for reinstament of Paved areas to original Status | m | 500
6.7 | Provide all materials and construct masonary walling Gate Valve chambers on reinforced concrete base,internal dimensions 1200mmx1200mm.include for supply and fixing of removable reinforced concrete cover slab,mild steel frame,lifting/opening mechanism,step irons,compacted granular fill,rendering of exposed blockwork etc.All as detailed as directed | Nr | 5
Volumetric Water Meter
6.8 | DN 80 | Nr | 2
6.9 | DN 50 | Nr | 1
Air Valve
Single Orifice Air Valve
6.1 | DN 50 | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
7 | FENCING
7.1 | Supply, transport to site and install @2500mmc/c concrete poles 2600mm tall and 500 cranked length with 100mmx100mm CS/area with provision for barbed wire line holes. Rate to include for excavation of pole pits and strainers (8) and firming with concrete at the poles base to repair the existing fence. | Nr | 60
7.2 | Supply and install 1500x2000mm single leave steel grill gate complete with iron mongery (use 50mmx25mmx6mm SHS with 38mmx25mmx6mm vertical members). Provide for epoxy primer paint with 2 coats of final gloss paint | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Kisii Package B
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No. Tender No. GWASCO/ CLSG II/KISII/02/2025/A______
PACKAGE 2: EXTENSION OF PIPELINES AND ASSOCIATED WORKS FOR KISII TOWN WATER PROJECT PACKAGE B
Construction of Water Distribution Pipeline (OD 75; Total Length 2.6km), Rehabilitation of Existing 250m3 Masonary Tank and Construction of a Solar Booster Station at Milimani Tanks Site
Amount
(Kshs)
Page Total, Page 2 of 10
Page Total, Page 4 of 10
Page Total, Page 6 of 10
Page Total, Page 7 of 10
Page Total, Page 8 of 10
Page Total, Page 9 of 10
Page Total, Page 9 of 12
Bill No. 1.1 Total (Exclusive of Value Added Tax - VAT) carried to Grand Summary Sheet

## Kisii Package B - Grand Summary
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No. Tender No. Tender No. GWASCO/ CLSG II/KISII/02/2025/B______
PACKAGE 2: EXTENSION OF PIPELINES AND ASSOCIATED WORKS FOR KISII TOWN WATER PROJECT PACKAGE B
GRAND SUMMARY
Bill | BILL DESCRIPTION | AMOUNT
Pacakge 2 | EXTENSION OF PIPELINES AND ASSOCIATED WORKS FOR KISII TOWN WATER PROJECT PACKAGE B
Construction of Water Distribution Pipeline (OD 75; Total Length 2.6km), Rehabilitation of Existing 250m3 Masonary Tank and Construction of a Solar Booster Station at Milimani
Package 2 Total (A)
Sub-Total [Excl. VAT]; (A)
Add 16% VAT (D = 16% of B)
Grand Total [Incl. 16% VAT]; (C = A+B)
Total Amount in words: Kenya Shilings
…….…………………………………………………………………………………………………………………………..……………………………………………….
Tenderer's signature and stamp……………………………….………………………………………………………….
Date…………………………………………………………………………………………………
Address ………………………………………………………………………………………

## Gensonso Water Project (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 3: REHABILITATION AND PIPELINE EXTENSION OF GESONSO WATER PROJECT
Construction and Rehabilitation of Water Distribution Pipelines (OD 63 - OD 160; Total Length 4.5km)
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
CLASS A: GENERAL ITEM
1.1 | Provide a provisional sum of Ksh 100,000 for wayleaves, permits and approvals | Item | PS |  | 100000
1.2 | Fabricate and install publicity boards clearly indicating the details of the project as directed by the engineer; | Nr | 2
1.3 | Provide a provisional sum of Ksh 100,000 for Branding as directed by the Engineer | Item | PS |  | 100000
A 2.1 | General Information and requirements
Specific conditions in execution of these Works are deemed to be included in the Contractor's rates. The Contractor will be required to submit Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include but are not limited to the following: i. No blasting will be permitted in these areas ii. The Contactor to maintain uninterrupted continuity of water supply in existing mains iii. Pedestrian and vehicular Access to individual shops / plots to be maintained at all times iv. Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v. Allow for method related costs for laying water mains across existing active lines with minimal disruption of flow vi. Allow for method related costs for dewatering of trenches.
A 2.2 | Cost relating to the above mentioned specific conditions
Allow for method related charges the tenderer feels may be required. These should be idicated below with pricing for each item
A 2.2.1 | i) | Item | LS
A 2.2.2 | ii) | Item | LS
A 2.3 | Survey Works
A 2.3.1 | Allow for Engineering Survey of the Proposed pipeline alignments including preparation of plan and profile with levels at 20m intervals horizontally | m | 4900
ESHS | Environmental, Social, Health and Safety (ESHS) Cost
ESHS 1 | Allow for any costs associated with compliance with environmental, health, and safety requirements in line with the Environmental and Social Management Plan (ESMP) provided for under Section IV of the technical specifications in the bid document. This compliance shall be consistent with the requirements of respective government agencies and prevailing legislation. The cost under this item shall include a quarterly environmental audit in the ESMP by a registered Lead Expert. | Item | PC
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A260 | Testing of works
A260.1 | Pipeline testing and commissioning of the Pipeline (Outer Diameter varying from 63-160mm ) including provision of all equipment, materials and works necessary for testing such as but not limited to thrust bloks, anchor blocks,provision, transportation and use of water, pipe fittings,disposal of used water. | m | 4900
A260.2 | Disinfection of Pipeline (Outer Diameter varying from 63-160mm) : flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disifecting water | m | 4900
CLASS D: DEMOLITION AND SITE CLEARANCE
D1 | General siteclearance along the pipeline allignment. | ha | 1
D2 | Tree Cutting (Provisional)
Cut down trees, grub up roots and cart away to tips
D2.1 | Girth: 1.0 m - 2 m | Nr | 10
Note:- Girth shall be measured 1.0m above ground level
D2.2 | Demolish existing concrete plinths along pipeline alignment and hand over material to the owner. | m2 | 100
D2.3 | Demolish existing temporary structures along pipeline allignment and hand over materials to the owner (Approximate area 10m²) | Nr | 50
CLASS I: PIPE WORK - PIPES
Supply, Transport to Site and Store
I7 | High Density Polyethylene Pipes (HDPE)
I71.1 | Nominal bore 63mm | m | 2900
I71.2 | Nominal bore 160mm | m | 2000
Transport from Site Store, Lay and Joint Pipes in Trench, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation trenches, Backfilling and final Reinstatement.
I7 | High Density Polyethylene Pipes (HDPE)
Nominal Bore 63 to 160mm in trenches
I712.1 | Depth not exceeding 1.5 m | m | 4900
CLASS J: PIPE WORK - FITTINGS AND VALVES - PN16
A | Supply, Transport to Site and Store
A-J3 | HDPE Pipe Fittings
A-J32 | Junction and Branches
HDPE Plain Ended TEE
A-J321.1 | OD 110 x OD 63 | Nr | 2
A-J321.2 | OD 110 x OD 50 | Nr | 5
A-J321.3 | OD 110 x OD 40 | Nr | 2
A-J321.4 | OD 63 x OD 40 | Nr | 3
A-J321.5 | OD 63 x OD 32 | Nr | 3
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A-J321.6 | OD 50 x OD 50 | Nr | 2
A-J321.7 | OD 50 x OD 32 | Nr | 3
A-J321.8 | OD 40 x OD 40 | Nr | 3
A-J321.9 | OD 32 x OD 32 | Nr | 3
A-J33 | Tapers
Plain Ended Concentric Taper
A-J331.1 | OD 63 x OD 50 | Nr | 2
A-J331.2 | OD 50 x OD 40 | Nr | 2
A-J331.3 | OD 40 x OD 32 | Nr | 2
A-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
A-J341.1 | OD 110 | Nr | 6
A-J341.2 | OD 63 | Nr | 6
A-J341.3 | OD 50 | Nr | 4
A-J341.4 | OD 40 | Nr | 8
A-J35 | Plain Ended Saddle Clamps
A-J351.1 | OD 63 x OD 50 | Nr | 2
A-J351.2 | OD 50 x OD 40 | Nr | 2
A-J351.3 | OD 40 x OD 32 | Nr | 2
A-J36 | Plain Ended Blank Flange
A-J361.1 | OD 110 | Nr | 1
A-J361.2 | OD 63 | Nr | 2
A-J361.3 | OD 50 | Nr | 2
A-J361.4 | OD 40 | Nr | 3
A-J361.5 | OD 32 | Nr | 3
A-J37 | Valves and Penstocks
A-J371 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
A-J371.1 | DN 100mm | Nr | 3
A-J371.2 | DN 50mm | Nr | 12
A-J371.3 | DN 40mm | Nr | 2
A-J371.4 | DN 32mm | Nr | 2
A-J38 | Air Valve
A-J381 | Single Orifice Air Valve
A-J381.1 | DN 50 | Nr | 5
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS J: PIPE WORK - FITTINGS AND VALVES
B | Transport from Site Store, Install and fix all the fittings in treches and chambers.
B-J3 | HDPE Pipe Fittings
B-J32 | Junction and Branches
HDPE Plain Ended TEE
B-J321.1 | OD 110 x OD 63 | Nr | 2
B-J321.2 | OD 110 x OD 50 | Nr | 5
B-J321.3 | OD 110 x OD 40 | Nr | 2
B-J321.4 | OD 63 x OD 40 | Nr | 3
B-J321.5 | OD 63 x OD 32 | Nr | 3
B-J321.6 | OD 50 x OD 50 | Nr | 2
B-J321.7 | OD 50 x OD 32 | Nr | 3
B-J321.8 | OD 40 x OD 40 | Nr | 3
B-J321.9 | OD 32 x OD 32 | Nr | 3
B-J33 | Tapers
Plain Ended Concentric Taper
B-J331.1 | OD 63 x OD 50 | Nr | 2
B-J331.2 | OD 50 x OD 40 | Nr | 2
B-J331.3 | OD 40 x OD 32 | Nr | 2
B-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
B-J341.1 | OD 110 | Nr | 6
B-J341.2 | OD 63 | Nr | 6
B-J341.3 | OD 50 | Nr | 4
B-J341.4 | OD 40 | Nr | 8
B-J35 | Plain Ended Saddle Clamps
B-J351.1 | OD 63 x OD 50 | Nr | 2
B-J351.2 | OD 50 x OD 40 | Nr | 2
B-J351.3 | OD 40 x OD 32 | Nr | 2
B-J36 | Plain Ended Blank Flange
B-J361.1 | OD 110 | Nr | 1
B-J361.2 | OD 63 | Nr | 2
B-J361.3 | OD 50 | Nr | 2
B-J361.4 | OD 40 | Nr | 3
B-J361.5 | OD 32 | Nr | 3
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
B-J37 | Valves and Penstocks
B-J371 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
B-J371.1 | DN 150mm | Nr | 2
B-J371.2 | DN 50mm | Nr | 12
B-J371.3 | DN 40mm | Nr | 2
B-J371.4 | DN 32mm | Nr | 2
B-J38 | Air Valve
B-J381 | Single Orifice Air Valve
B-J381.1 | DN 50 | Nr | 3
CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, Reinforcement, Formwork, Joints and Finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
K11 | IN SITU MASONRY CHAMBERS
K12 | Depth not exceeding 1.5m
K212.1 | Provide all materials and construct masonry walling for GATE/AIR VALVE Chambers on Reinforced Concrete Base, internal dimensions 1200mm x 1200mm. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc; | Nr | 8
K6 | Crossings
K642 | Allow for crossing fences,existing hedges & masonry fences and reinstating these after completion of the construction works | m | 100
K652 | Allow for crossing existing drains and reinstatement after completion of the construction works. Include for provision of a divertion and keeping it operational during construction. | m | 50
K662 | Allow for crossing existing underground services(water lines, sewerlines, telephone/electricity ducts, fibre optic cableduct etc.) including reistatement to the original status and liason with the relevant body for inspection/approval during execution of the works. Pilot excavation shall be done to establish exact location of any buried services prior to actual excavation. The rate shall be demeed to include for pilot excavations, repairs and reistatement of any damages to the existing buried services as a result of execution of the works. | Item | LS
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K7 | Relocation / Reinstatement
K732.1 | Breaking up, Temporary and Permanent Reinstatement of MURRAM road with 300mm thick well graded stabilised gravel with 3% cement content base compacted in layers of 150mm thick using an 8-10 tonne roller. Contractor to allow for provision of requisite diversion signage, controls and safety precaution in his rates | m | 100
K732.2 | Breaking up temporary and permanent reinstatement of paved footpaths (concrete, cabro, tarmac, etc.). Pipe bore not exceeding 150mm | m | 100
K8 | Other Pipework Ancillaries
K82 | Excavate for, supply and fix concrete Marker Posts along the the water main route, road crossings, change of direction, air valves, washouts and valve chambers at locations shown by the Engineer. All in accordance with details given in the standard drawings. | Nr | 40
CLASS L:- PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
L1 | Extras over excavation and backfilling for excavation in Rock. Rate to include carting away and disposal. (Provisional)
L11 | In pipe trench and chambers
L111.2 | Excavation in trench for rock class "B" | m³ | 150
Note:- Blasting is NOT permitted for Item L11
L7 | Concrete Support, Thrust Blocks, Stools and Anchor Blocks
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc
Class 20/20 Mass Concrete Thrust Blocks
NOTE:- The work includes pipe and fitting fixing
L71 | Volume:- Not exceeding 0.1 m³
L711 | To pipes nominal bore: 110mm | Nr | 5
CLASS V: PAINTING
V510 | Allow for Cleaning and Painting with 3 Coats of approved Epoxy paint on all exposed pipework, fittings, valves, etc, to Engineers Approval. | m2 | 20
New Connections
| Allow a Provisional Sum of Kshs 250,000 for transfer of existing connections from existing pipelines to new pipelines and new connections. Include for saddle clamps, stop cocks, control valves, etc | Item | PS |  | 250000
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Gensonso Water (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 3: REHABILITATION AND PIPELINE EXTENSION OF GESONSO WATER PROJECT
Construction and Rehabilitation of Water Distribution Pipelines (OD 63 - OD 160; Total Length 4.5km)
Amount
(Kshs)
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill No. 1.1 Total (Exclusive of Value Added Tax - VAT) carried to Grand Summary Sheet

## Gensonso Water - Grand Sum (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 3: REHABILITATION AND PIPELINE EXTENSION OF GESONSO WATER PROJECT
GRAND SUMMARY
Bill | BILL DESCRIPTION | AMOUNT
Pacakge 3 | REHABILITATION AND PIPELINE EXTENSION OF GESONSO WATER PROJECT
Construction and Rehabilitation of Water Distribution Pipelines (OD 63 - OD 160; Total Length 4.5km)
Package 1 Total (A)
Sub-Total [Excl. VAT]; (A)
Add 5% Contingencies (B)
Total [Excl. VAT]; (C = A+B)
Add 16% VAT (D = 16% of C)
Grand Total [Incl. 16% VAT]; (E = C+D)

## Nyansiongo Water Project (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 4: PIPELINE EXTENSION FOR NYANSIONGO WATER PROJECT
Construction of Water Distribution Extension Pipeline (OD 40 - OD 90; Total Length 4.2km)
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
CLASS A: GENERAL ITEM
1.1 | Provide a provisional sum of Ksh 100,000 for wayleaves, permits and approvals | Item | PS |  | 100000
1.2 | Fabricate and install publicity boards clearly indicating the details of the project as directed by the engineer; | Nr | 2
A 2.1 | General Information and requirements
Specific conditions in execution of these Works are deemed to be included in the Contractor's rates. The Contractor will be required to submit Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include but are not limited to the following: i. No blasting will be permitted in these areas ii. The Contactor to maintain uninterrupted continuity of water supply in existing mains iii. Pedestrian and vehicular Access to individual shops / plots to be maintained at all times iv. Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v. Allow for method related costs for laying water mains across existing active lines with minimal disruption of flow vi. Allow for method related costs for dewatering of trenches.
A 2.2 | Cost relating to the above mentioned specific conditions
Allow for method related charges the tenderer feels may be required. These should be idicated below with pricing for each item
A 2.2.1 | i)Diversion of Traffic | Item | LS
A 2.2.2 | ii) | Item | LS
A 2.3 | Survey Works
A 2.3.1 | Allow for Engineering Survey of the Proposed pipeline alignments including preparation of plan and profile with levels at 20m intervals horizontally | m | 4200
ESHS | Environmental, Social, Health and Safety (ESHS) Cost
ESHS 1 | Allow for any costs associated with compliance with environmental, health, and safety requirements in line with the Environmental and Social Management Plan (ESMP) provided for under Section IV of the technical specifications in the bid document. This compliance shall be consistent with the requirements of respective government agencies and prevailing legislation. The cost under this item shall include a quarterly environmental audit in the ESMP by a registered Lead Expert. | Item | PC
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A260 | Testing of works
A260.1 | Pipeline testing and commissioning of the Pipeline (Outer Diameter varying from 40-90mm ) including provision of all equipment, materials and works necessary for testing such as but not limited to thrust bloks, anchor blocks,provision, transportation and use of water, pipe fittings,disposal of used water. | m | 4200
A260.2 | Disinfection of Pipeline (Outer Diameter varying from 40-90mm) : flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disifecting water | m | 4200
CLASS D: DEMOLITION AND SITE CLEARANCE
D1 | General siteclearance along the pipeline allignment. | ha | 5
D2 | Tree Cutting (Provisional)
Cut down trees, grub up roots and cart away to tips
D2.1 | Girth: 1.0 m - 2 m | Nr | 20
Note:- Girth shall be measured 1.0m above ground level
D2.2 | Demolish existing concrete plinths along pipeline alignment and hand over material to the owner. | m2 | 100
D2.3 | Demolish existing temporary structures along pipeline allignment and hand over materials to the owner (Approximate area 10m²) | Nr | 50
CLASS I: PIPE WORK - PIPES
Supply, Transport to Site and Store
I7 | High Density Polyethylene Pipes (HDPE)
I71.1 | OD 40mm PN 10 | m | 500
I71.2 | OD 50mm PN 10 | m | 500
I71.3 | OD 63mm PN10 | m | 1000
I71.4 | OD 90mm PN 12 | m | 2200
Transport from Site Store, Lay and Joint Pipes in Trench, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation trenches, Backfilling and final Reinstatement.
I7 | High Density Polyethylene Pipes (HDPE)
Nominal Bore 40 to 90mm in trenches
I712.1 | Depth not exceeding 1.5 m | m | 4200
CLASS J: PIPE WORK - FITTINGS AND VALVES - PN16
A | Supply, Transport to Site and Store
A-J3 | HDPE Pipe Fittings
A-J31 | Bends nominal bore 90mm
A-J311.1 | 90° | Nr | 2
A-J311.2 | 45° | Nr | 4
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A-J32 | Junction and Branches
HDPE Plain Ended TEE
A-J321.1 | OD 110 x OD 63 | Nr | 2
A-J321.2 | OD 110 x OD 40 | Nr | 2
A-J321.3 | OD 63 x OD 40 | Nr | 3
A-J321.4 | OD 63 x OD 32 | Nr | 3
A-J321.5 | OD 50 x OD 50 | Nr | 2
A-J321.6 | OD 50 x OD 32 | Nr | 3
A-J321.7 | OD 40 x OD 40 | Nr | 3
A-J321.8 | OD 32 x OD 32 | Nr | 3
A-J33 | Tapers
Plain Ended Concentric Taper
A-J331.1 | OD 63 x OD 50 | Nr | 2
A-J331.2 | OD 50 x OD 40 | Nr | 2
A-J331.3 | OD 40 x OD 32 | Nr | 2
A-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
A-J341.1 | OD 63 | Nr | 2
A-J341.2 | OD 50 | Nr | 2
A-J341.3 | OD 40 | Nr | 4
A-J341.4 | OD 32 | Nr | 2
A-J35 | Plain Ended Saddle Clamps
A-J351.1 | OD 63 x OD 50 | Nr | 2
A-J351.2 | OD 50 x OD 40 | Nr | 2
A-J351.3 | OD 40 x OD 32 | Nr | 2
A-J36 | Plain Ended Blank Flange
A-J361.1 | OD 63 | Nr | 2
A-J361.2 | OD 50 | Nr | 2
A-J361.3 | OD 40 | Nr | 3
A-J361.4 | OD 32 | Nr | 3
A-J37 | Valves and Penstocks
A-J371 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
A-J371.1 | DN 50mm | Nr | 1
A-J371.2 | DN 40mm | Nr | 2
A-J371.3 | DN 32mm | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A-J38 | Air Valve
A-J381 | Single Orifice Air Valve
A-J381.1 | DN 50 | Nr | 2
CLASS J: PIPE WORK - FITTINGS AND VALVES
B | Transport from Site Store, Install and fix all the fittings in treches and chambers.
B-J3 | HDPE Pipe Fittings
B-J31 | Bends nominal bore 90mm
B-J311.1 | 90° | Nr | 2
B-J311.2 | 45° | Nr | 4
B-J32 | Junction and Branches
HDPE Plain Ended TEE
B-J321.1 | OD 110 x OD 63 | Nr | 2
B-J321.2 | OD 110 x OD 40 | Nr | 2
B-J321.3 | OD 63 x OD 40 | Nr | 3
B-J321.4 | OD 63 x OD 32 | Nr | 3
B-J321.5 | OD 50 x OD 50 | Nr | 2
B-J321.6 | OD 50 x OD 32 | Nr | 3
B-J321.7 | OD 40 x OD 40 | Nr | 3
B-J321.8 | OD 32 x OD 32 | Nr | 3
B-J33 | Tapers
Plain Ended Concentric Taper
B-J331.1 | OD 63 x OD 50 | Nr | 2
B-J331.2 | OD 50 x OD 40 | Nr | 2
B-J331.3 | OD 40 x OD 32 | Nr | 2
B-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
B-J341.1 | OD 63 | Nr | 2
B-J341.2 | OD 50 | Nr | 2
B-J341.3 | OD 40 | Nr | 4
B-J341.4 | OD 32 | Nr | 2
B-J35 | Plain Ended Saddle Clamps
B-J351.1 | OD 63 x OD 50 | Nr | 2
B-J351.2 | OD 50 x OD 40 | Nr | 2
B-J351.3 | OD 40 x OD 32 | Nr | 2
B-J36 | Plain Ended Blank Flange
B-J361.1 | OD 63 | Nr | 2
B-J361.2 | OD 50 | Nr | 2
B-J361.3 | OD 40 | Nr | 3
B-J361.4 | OD 32 | Nr | 3
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
B-J37 | Valves and Penstocks
B-J371 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
B-J371.1 | DN 50mm | Nr | 1
B-J371.2 | DN 40mm | Nr | 2
B-J371.3 | DN 32mm | Nr | 2
B-J38 | Air Valve
B-J381 | Single Orifice Air Valve
B-J381.1 | DN 50 | Nr | 2
CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, Reinforcement, Formwork, Joints and Finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
K11 | IN SITU MASONRY CHAMBERS
K12 | Depth not exceeding 1.5m
K212.1 | Provide all materials and construct masonry walling for GATE/AIR VALVE Chambers on Reinforced Concrete Base, internal dimensions 1200mm x 1200mm. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc; | Nr | 8
K6 | Crossings
K642 | Allow for crossing fences,existing hedges & masonry fences and reinstating these after completion of the construction works | m | 100
K652 | Allow for crossing existing drains and reinstatement after completion of the construction works. Include for provision of a divertion and keeping it operational during construction. | m | 50
K662 | Allow for crossing existing underground services(water lines, sewerlines, telephone/electricity ducts, fibre optic cableduct etc.) including reistatement to the original status and liason with the relevant body for inspection/approval during execution of the works. Pilot excavation shall be done to establish exact location of any buried services prior to actual excavation. The rate shall be demeed to include for pilot excavations, repairs and reistatement of any damages to the existing buried services as a result of execution of the works. | Item | LS
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K7 | Relocation / Reinstatement
K732.1 | Breaking up, Temporary and Permanent Reinstatement of MURRAM road with 300mm thick well graded stabilised gravel with 3% cement content base compacted in layers of 150mm thick using an 8-10 tonne roller. Contractor to allow for provision of requisite diversion signage, controls and safety precaution in his rates | m | 100
K732.2 | Breaking up temporary and permanent reinstatement of paved footpaths (concrete, cabro, tarmac, etc.). Pipe bore not exceeding 150mm | m | 100
K8 | Other Pipework Ancillaries
K82 | Excavate for, supply and fix concrete Marker Posts along the the water main route, road crossings, change of direction, air valves, washouts and valve chambers at locations shown by the Engineer. All in accordance with details given in the standard drawings. | Nr | 45
CLASS L:- PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
L1 | Extras over excavation and backfilling for excavation in Rock. Rate to include carting away and disposal. (Provisional)
L11 | In pipe trench and chambers
L111.1 | Excavation in trench for rock class "A" | m³ | 400
L111.2 | Excavation in trench for rock class "B" | m³ | 700
Note:- Blasting is NOT permitted for Item L11
L7 | Concrete Support, Thrust Blocks, Stools and Anchor Blocks
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc
Class 20/20 Mass Concrete Thrust Blocks
NOTE:- The work includes pipe and fitting fixing
L71 | Volume:- Not exceeding 0.1 m³
L711 | To pipes nominal bore: 110mm | Nr | 20
CLASS V: PAINTING
V510 | Allow for Cleaning and Painting with 3 Coats of approved Epoxy paint on all exposed pipework, fittings, valves, etc, to Engineers Approval. | m2 | 20
New Connections
| Allow a Provisional Sum of Kshs 100,000 for transfer of existing connections from existing pipelines to new pipelines and new connections. Include for saddle clamps, stop cocks, control valves, etc | Item | PS |  | 100000
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Nyansiongo Water (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 4: PIPELINE EXTENSION FOR NYANSIONGO WATER PROJECT
Construction of Water Distribution Extension Pipeline (OD 40 - OD 90; Total Length 4.2km)
Amount
(Kshs)
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill No. 1.1 Total (Exclusive of Value Added Tax - VAT) carried to Grand Summary Sheet

## Nyansiongo Water - Grand Sum (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 4: PIPELINE EXTENSION FOR NYANSIONGO WATER PROJECT
GRAND SUMMARY
Bill | BILL DESCRIPTION | AMOUNT
Pacakge 4 | PIPELINE EXTENSION FOR NYANSIONGO WATER PROJECT
Construction of Water Distribution Extension Pipeline (OD 40 - OD 90; Total Length 4.2km)
Package 1 Total (A)
Sub-Total [Excl. VAT]; (A)
Add 5% Contingencies (B)
Total [Excl. VAT]; (C = A+B)
Add 16% VAT (D = 16% of C)
Grand Total [Incl. 16% VAT]; (E = C+D)

## Nyamira Town Water Project (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 5: PIPELINE EXTENSION FOR NYAMIRA TOWN WATER PROJECT
Construction of Water Distribution Pipeline (OD 50 - OD 63; Total Length 4.2km)
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
CLASS A: GENERAL ITEM
1.1 | Provide a provisional sum of Ksh 100,000 for wayleaves, permits and approvals | Item | PS |  | 100000
1.2 | Fabricate and install publicity boards clearly indicating the details of the project as directed by the engineer; | Nr | 2
1.3 | Provide a provisional sum of Ksh 100,000 for Branding as directed by the Engineer | Item | PS |  | 100000
A 2.1 | General Information and requirements
Specific conditions in execution of these Works are deemed to be included in the Contractor's rates. The Contractor will be required to submit Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include but are not limited to the following: i. No blasting will be permitted in these areas ii. The Contactor to maintain uninterrupted continuity of water supply in existing mains iii. Pedestrian and vehicular Access to individual shops / plots to be maintained at all times iv. Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v. Allow for method related costs for laying water mains across existing active lines with minimal disruption of flow vi. Allow for method related costs for dewatering of trenches.
A 2.2 | Cost relating to the above mentioned specific conditions
Allow for method related charges the tenderer feels may be required. These should be idicated below with pricing for each item
A 2.2.1 | i) | Item | LS
A 2.2.2 | ii) | Item | LS
A 2.3 | Survey Works
A 2.3.1 | Allow for Engineering Survey of the Proposed pipeline alignments including preparation of plan and profile with levels at 20m intervals horizontally | m | 4500
ESHS | Environmental, Social, Health and Safety (ESHS) Cost
ESHS 1 | Allow for any costs associated with compliance with environmental, health, and safety requirements in line with the Environmental and Social Management Plan (ESMP) provided for under Section IV of the technical specifications in the bid document. This compliance shall be consistent with the requirements of respective government agencies and prevailing legislation. The cost under this item shall include a quarterly environmental audit in the ESMP by a registered Lead Expert. | Item | PC
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A260 | Testing of works
A260.1 | Pipeline testing and commissioning of the Pipeline (Outer Diameter varying from 32-110mm ) including provision of all equipment, materials and works necessary for testing such as but not limited to thrust bloks, anchor blocks,provision, transportation and use of water, pipe fittings,disposal of used water. | m | 3700
A260.2 | Disinfection of Pipeline (Outer Diameter varying from 32-110mm) : flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disifecting water | m | 3700
CLASS D: DEMOLITION AND SITE CLEARANCE
D1 | General siteclearance along the pipeline allignment. | ha | 1
D2 | Tree Cutting (Provisional)
Cut down trees, grub up roots and cart away to tips
D2.1 | Girth: 1.0 m - 2 m | Nr | 29
Note:- Girth shall be measured 1.0m above ground level
D2.2 | Demolish existing concrete plinths along pipeline alignment and hand over material to the owner. | m2 | 50
D2.3 | Demolish existing temporary structures along pipeline allignment and hand over materials to the owner (Approximate area 10m²) | Nr | 50
CLASS I: PIPE WORK - PIPES
Supply, Transport to Site and Store
I7 | High Density Polyethylene Pipes (HDPE)
I71.1 | OD 32mm | m | 800
I71.2 | OD 40mm | m | 800
I71.3 | OD 50mm | m | 800
I71.4 | OD 63mm | m | 800
I71.5 | OD 110mm | m | 500
Transport from Site Store, Lay and Joint Pipes in Trench, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation trenches, Backfilling and final Reinstatement.
I7 | High Density Polyethylene Pipes (HDPE)
Nominal Bore 32 to 110mm in trenches
I712.1 | Depth not exceeding 1.5 m | m | 3700
CLASS J: PIPE WORK - FITTINGS AND VALVES - PN16
A | Supply, Transport to Site and Store
A-J3 | HDPE Pipe Fittings
A-J31 | Bends nominal bore 110mm
A-J311.1 | 90° | Nr | 2
A-J311.2 | 45° | Nr | 4
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A-J32 | Junction and Branches
HDPE Plain Ended TEE
A-J321.1 | OD 110 x OD 63 | Nr | 2
A-J321.2 | OD 110 x OD 50 | Nr | 5
A-J321.3 | OD 110 x OD 40 | Nr | 2
A-J321.4 | OD 63 x OD 40 | Nr | 3
A-J321.5 | OD 63 x OD 32 | Nr | 3
A-J321.6 | OD 50 x OD 50 | Nr | 2
A-J321.7 | OD 50 x OD 32 | Nr | 3
A-J321.8 | OD 40 x OD 40 | Nr | 3
A-J321.9 | OD 32 x OD 32 | Nr | 3
A-J33 | Tapers
Plain Ended Concentric Taper
A-J331.1 | OD 63 x OD 50 | Nr | 2
A-J331.2 | OD 50 x OD 40 | Nr | 2
A-J331.3 | OD 40 x OD 32 | Nr | 2
A-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
A-J341.1 | OD 110 | Nr | 6
A-J341.2 | OD 63 | Nr | 6
A-J341.3 | OD 50 | Nr | 4
A-J341.4 | OD 40 | Nr | 8
A-J35 | Plain Ended Saddle Clamps
A-J351.1 | OD 63 x OD 50 | Nr | 2
A-J351.2 | OD 50 x OD 40 | Nr | 2
A-J351.3 | OD 40 x OD 32 | Nr | 2
A-J36 | Plain Ended Blank Flange
A-J361.1 | OD 110 | Nr | 1
A-J361.2 | OD 63 | Nr | 2
A-J361.3 | OD 50 | Nr | 2
A-J361.4 | OD 40 | Nr | 3
A-J361.5 | OD 32 | Nr | 3
A-J37 | Valves and Penstocks
A-J371 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
A-J371.1 | DN 100mm | Nr | 3
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A-J371.2 | DN 50mm | Nr | 12
A-J371.3 | DN 40mm | Nr | 2
A-J371.4 | DN 32mm | Nr | 2
A-J38 | Air Valve
A-J381 | Single Orifice Air Valve
A-J381.1 | DN 50 | Nr | 6
CLASS J: PIPE WORK - FITTINGS AND VALVES
B | Transport from Site Store, Install and fix all the fittings in treches and chambers.
B-J3 | HDPE Pipe Fittings
B-J31 | Bends nominal bore 110mm
B-J311.1 | 90° | Nr | 2
B-J311.2 | 45° | Nr | 4
B-J32 | Junction and Branches
HDPE Plain Ended TEE
B-J321.1 | OD 110 x OD 63 | Nr | 2
B-J321.2 | OD 110 x OD 50 | Nr | 5
B-J321.3 | OD 110 x OD 40 | Nr | 2
B-J321.4 | OD 63 x OD 40 | Nr | 3
B-J321.5 | OD 63 x OD 32 | Nr | 3
B-J321.6 | OD 50 x OD 50 | Nr | 2
B-J321.7 | OD 50 x OD 32 | Nr | 3
B-J321.8 | OD 40 x OD 40 | Nr | 3
B-J321.9 | OD 32 x OD 32 | Nr | 3
B-J33 | Tapers
Plain Ended Concentric Taper
B-J331.1 | OD 63 x OD 50 | Nr | 2
B-J331.2 | OD 50 x OD 40 | Nr | 2
B-J331.3 | OD 40 x OD 32 | Nr | 2
B-J34 | Plain Ended Flange Adaptors
HDPE Butt fusion stub ends complete with Metallic-Stub flange, Bolts, Nuts and Washers
B-J341.1 | OD 110 | Nr | 6
B-J341.2 | OD 63 | Nr | 6
B-J341.3 | OD 50 | Nr | 4
B-J341.4 | OD 40 | Nr | 8
B-J35 | Plain Ended Saddle Clamps
B-J351.1 | OD 63 x OD 50 | Nr | 2
B-J351.2 | OD 50 x OD 40 | Nr | 2
B-J351.3 | OD 40 x OD 32 | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
B-J36 | Plain Ended Blank Flange
B-J361.1 | OD 110 | Nr | 1
B-J361.2 | OD 63 | Nr | 2
B-J361.3 | OD 50 | Nr | 2
B-J361.4 | OD 40 | Nr | 3
B-J361.5 | OD 32 | Nr | 3
B-J37 | Valves and Penstocks
B-J371 | All Flanged Gate Valve
Gate Valves for Washouts and Line Valves to be supplied complete with extension Spindle n.e. 3.0m and Tee- key. Isolating Gate Valves to Air Valves to have hand wheels. Contractor's rates to include for this
B-J371.1 | DN 100mm | Nr | 3
B-J371.2 | DN 50mm | Nr | 12
B-J371.3 | DN 40mm | Nr | 2
B-J371.4 | DN 32mm | Nr | 2
B-J38 | Air Valve
B-J381 | Single Orifice Air Valve
B-J381.1 | DN 50 | Nr | 6
CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, Reinforcement, Formwork, Joints and Finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
K11 | IN SITU MASONRY CHAMBERS
K12 | Depth not exceeding 1.5m
K212.1 | Provide all materials and construct masonry walling for GATE/AIR VALVE Chambers on Reinforced Concrete Base, internal dimensions 1200mm x 1200mm. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc; | Nr | 8
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K6 | Crossings
K642 | Allow for crossing fences,existing hedges & masonry fences and reinstating these after completion of the construction works | m | 100
K652 | Allow for crossing existing drains and reinstatement after completion of the construction works. Include for provision of a divertion and keeping it operational during construction. | m | 50
K662 | Allow for crossing existing underground services(water lines, sewerlines, telephone/electricity ducts, fibre optic cableduct etc.) including reistatement to the original status and liason with the relevant body for inspection/approval during execution of the works. Pilot excavation shall be done to establish exact location of any buried services prior to actual excavation. The rate shall be demeed to include for pilot excavations, repairs and reistatement of any damages to the existing buried services as a result of execution of the works. | Item | LS
K7 | Relocation / Reinstatement
K732.1 | Breaking up, Temporary and Permanent Reinstatement of MURRAM road with 300mm thick well graded stabilised gravel with 3% cement content base compacted in layers of 150mm thick using an 8-10 tonne roller. Contractor to allow for provision of requisite diversion signage, controls and safety precaution in his rates | m | 100
K732.2 | Breaking up temporary and permanent reinstatement of paved footpaths (concrete, cabro, tarmac, etc.). Pipe bore not exceeding 150mm | m | 100
K8 | Other Pipework Ancillaries
K82 | Excavate for, supply and fix concrete Marker Posts along the the water main route, road crossings, change of direction, air valves, washouts and valve chambers at locations shown by the Engineer. All in accordance with details given in the standard drawings. | Nr | 35
CLASS L:- PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
L1 | Extras over excavation and backfilling for excavation in Rock. Rate to include carting away and disposal. (Provisional)
L11 | In pipe trench and chambers
L111.1 | Excavation in trench for rock class "A" | m³ | 400
L111.2 | Excavation in trench for rock class "B" | m³ | 500
L111.3 | Excavation in trench for rock class "C" | m³ | 500
Note:- Blasting is NOT permitted for Item L11
L7 | Concrete Support, Thrust Blocks, Stools and Anchor Blocks
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc
Class 20/20 Mass Concrete Thrust Blocks
NOTE:- The work includes pipe and fitting fixing
L71 | Volume:- Not exceeding 0.1 m³
L711 | To pipes nominal bore: 110mm | Nr | 20
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS V: PAINTING
V510 | Allow for Cleaning and Painting with 3 Coats of approved Epoxy paint on all exposed pipework, fittings, valves, etc, to Engineers Approval. | m2 | 20
New Connections
| Allow a Provisional Sum of Kshs 250,000 for transfer of existing connections from existing pipelines to new pipelines and new connections. Include for saddle clamps, stop cocks, control valves, etc | Item | PS |  | 250000
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Nyamira Town Water (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 5: PIPELINE EXTENSION FOR NYAMIRA TOWN WATER PROJECT
Construction of Water Distribution Pipeline (OD 50 - OD 63; Total Length 4.2km)
Amount
(Kshs)
Page Total, Page 1 of 7
Page Total, Page 2 of 7
Page Total, Page 3 of 7
Page Total, Page 4 of 7
Page Total, Page 5 of 7
Page Total, Page 6 of 7
Page Total, Page 7 of 7
Bill No. 1.1 Total (Exclusive of Value Added Tax - VAT) carried to Grand Summary Sheet

## Nyamira Town Water - Grand Su (hidden)
WATER AND SANITATION DEVELOPMENT PROJECT (WSDP) - CONDITIONAL LIQUIDITY SUPPORT GRANT (CLSG) II
Tender No.
PACKAGE 5: PIPELINE EXTENSION FOR NYAMIRA TOWN WATER PROJECT
GRAND SUMMARY
Bill | BILL DESCRIPTION | AMOUNT
Pacakge 5 | PIPELINE EXTENSION FOR NYAMIRA TOWN WATER PROJECT
Construction of Water Distribution Pipeline (OD 50 - OD 63; Total Length 4.2km)
Package 1 Total (A)
Sub-Total [Excl. VAT]; (A)
Add 5% Contingencies (B)
Total [Excl. VAT]; (C = A+B)
Add 16% VAT (D = 16% of C)
Grand Total [Incl. 16% VAT]; (E = C+D)

## Grand Summary (hidden)
GRAND SUMMARY
CONSTRUCTION WORKS FOR KABETE - OLESERENI PIPELINE, WEST AND SOUTH NAIROBI WATER AND SEWERAGE PROJECT
BID No. AWWDA/AFD/NWSP/W-02/2022
BILL No. | DESCRIPTION |  | AMOUNT
(Kshs)
1 | Preliminary and General Items
0
2.1 | Kabete-Olesereni Pipeline (Supply of Pipes, Fittings, Valves and Ancillaries; DN 600, Total length 19.62 km) |  | #REF!
#REF!
2.2 | Kabete-Olesereni Pipeline (Pipeline Construction; DN 600, Total length 19.62 km) |  | #REF!
3.1 | Wilson Distribution Main, Line WL02 (DN 600; Total length 4.25 km) |  | #REF!
#REF!
3.2 | Extension of Water Reticulation Network within Wilson Area (OD 63 - OD 250; Total length 2.86 km) |  | #REF!
3.3 | Extension of Water Reticulation Network within area around Ngong Forest (OD 63 - OD 250; Total length 2.53 km) |  | #REF!
3.4 | Extension of Water Reticulation Network within Karen Plains (OD 63 - OD 110; Total length 8.6 km) |  | #REF!
3.5 | Kabiria Distribution Main, Line KB01 (OD355; Total length 1.57 km) |  | 0
3.6 | Extension of Water Water Reticulation Network within Kabiria (OD 63 - OD 160; Total length 16.19 km) |  | #REF!
3.7 | Extension of Water Reticulation Network within Kangemi and Kawangware Area (OD 63 - OD 110; Total length 5.17 km) |  | #REF!
3.8 | Extension of Water Reticulation Network within Kirigu (OD 63 - OD 110; Total length 7.17 km) |  | #REF!
3.9 | Household Water Connections (850 Nr) |  | #REF!
4.1 | Uthiru Storage Reservoir (2Nr Tanks, Each of Capacity 5,500m3) |  | #REF! | #REF!
4.2 | Karen Storage Reservoir (5,500 m3 Capacity) |  | #REF! | #REF!
| Bills Total Exclusive of VAT | (A) | #REF!
|  |  | #REF! | #REF!
| Add 7.5% of (A) for General and Physical Contingencies | (B)
| Bill Total Inclusive of Contingencies [A + B] | (C) | #REF!
#REF!
| Value Added Tax (VAT) - 16% of (C) | (D)
| GRAND TOTAL CARRIED TO LETTER OF BID | (C+D) | #REF!
#REF!
2193686627.97
Bills Total Exclusive of VAT | (A)
Add 10% of (A) for Contingencies | (B)
Bill Total Inclusive of Contingencies | (C)
Value Added Tax (VAT) - 16% of (C) | (D)
GRAND TOTAL CARRIED TO LETTER OF BID [(C) + (D)]

## Unit Rate (hidden)
CKE1135 - NAIROBI WATER AND SANITATION PROJECT
CONSTRUCTION WORKS FOR KABETE-OLESERENI PIPELINE, WEST AND SOUTH NAIROBI WATER AND SEWERAGE PROJECT
BID No. AWWDA/AFD/NWSP/W-02/2022
RETICULATION SEWERS
ITEM No. | DESCRIPTION | UNIT | QTY | RATE (Kshs) | AMOUNT (Kshs)
CLASS A | GENERAL ITEMS
Specified Requirements
Testing of works
Allow for water testing of sewers and manholes as specified including water for testing, requisite Materials, Personnel, Testing Equipment etc. and safe disposal of used water.
[7 empty] | 10 | m3 | 8250 | 25.9215 | 25.9215
4.1-A260.1 | 200mm Diameter Sewer pipe | m |  | 25 |  |  | 0.03142 |  | 318.2686 | m
4.1-A260.2 | 300mm Diameter Sewer pipe | m |  | 58 |  |  |  |  | 8250 | 58.3234 | 69.988
[7 empty] | 0.070695 |  | 141.4527
Allow for cleaning and flushing of Existing Sewer Line sections to which new sewers are to be connected so as to dislodge sediments, stones and other debris. Rate to include provision of all the equipment, materials and labour as may be required for physical removal of debris
4.1-A260.3 | 200mm Diameter Sewer pipe | m |  | 32
4.1-A260.4 | 300mm Diameter Sewer pipe | m |  | 73
0.03142
4.1-A260.5 | 450mm Diameter Sewer pipe | m |  | 164.25 |  |  |  | 0.070695
PAGE TOTAL CARRIED TO COLLECTION SHEET | [7 empty] | 0.15906 | 2.25
Temporary Works
4.1-A271 | Allow for temporary works for diversion of traffic during construction of sewers across roads, including sign posting, liaison with Traffic Police Department, County Authority, etc. all to the satisfaction of the Engineer. Include provision for maintaining temporary vehicular access to individual plots at all times. | Item |  | 500000
4.1-A277 | Allow for keeping trenches and other excavation free of water which may have entered through ground seepage, surface run-off or by other means as directed by the Engineer. | Item |  | 500000
A3 | Method Related Charges
A35 | Temporary Works
4.1-A353 | Allow for provision of Temporary Access to the Individual Plots or Business Premises during the Construction Works, approximate length of Access Structures of 4m. | Nr |  | 30000
4.1-A359.1 | Working within allowable Road Reserves, include costs for double / multiple handling of excavated materials if required. | Item | L.S | 250000
4.1-A359.2 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item:
| i) | Item | L.S | 100000
| ii) | Item | L.S | 100000
CLASS B | SITE INVESTIGATION
4.1-B111 | Allow for pilot excavation to identify and establish the exact location of underground services such as Sewers, Water Pipes, Fiber Cable, etc. prior to actual excavation as directed by the Engineer. Depth n.e 3m | nr |  | 1200 |  |  | 188.52
CLASS D | DEMOLITION AND SITE CLEARANCE
Rate to include for removal of debris, carting away and disposal to tips identified by the Contractor in liaison with Local Authorities
General clearance
4.1-D110 | Demolish and cart away natural and artificial articles, objects and obstructions which are above the original surface, n.e 3m on either side of the sewer lines | ha |  | 40000 |  |  | 500000
Cut down trees, grub up roots and cart away debris to designated spoil pit (Provisional)
4.1-D210.1 | Trees with Girth: 500mm - 1m | Nr |  | 1200
4.1-D210.2 | Trees with Girth: 1m - 2m | Nr |  | 1440
4.1-D220.1 | Trees with Girth: 2m - 3m | Nr |  | 1600
PAGE TOTAL CARRIED TO COLLECTION SHEET
4.1-D220.2 | Trees with Girth over 3m | Nr |  | 2000
4.1-D310 | Stumps with diameter less than 1m | Nr |  | 1600
4.1-D320 | Stumps with diameter exceeding 1m | Nr |  | 2400
4.1-D524 | Allow for demolition of Concrete Structures (including Inverted Block Drains) along the sewer alignment. Rate to include requisite reinstatement Works | m3 |  | 15000 |  |  | 8000000 | 800000
4.1-D534 | Allow for demolition of Masonry Structures along the sewer alignment (including Stone-pitched Drains). Rate to include requisite reinstatement Works | m² |  | 1600
CLASS E | EARTHWORKS
E4 | General Excavation
4.1-E424 | Excavation to trenching surface commencing from original ground level; depth n.e. 2.0m | m3 |  | 250
4.1-E434 | Extra over excavation in rock to achieve trenching surface; depth n.e. 2.0m (all rock classes) | m3 |  | 1250
E5 | Excavation Ancillaries
4.1-E532 | Disposal of excess excavated material | m3 |  | 80
4.1-E533 | Disposal of excess excavated rock | m3 |  | 160
4.1-E542 | Double handling of excavated material | m3 |  | 160
E6 | Filling
4.1-E634 | Selected excavated material from stack, fill and ram the materials around trench to achieve finished ground levels as directed by the Engineer | m3 |  | 80
4.1-E635 | Approved import granular material and fill and ram materials around trench to achieve finished ground levels as directed by the Engineer | m3 |  | 370
CLASS I | PIPEWORK - SEWERS
I4 | Steel Pipes
Provide, lay, and joint Steel Pipes (PN10) Sleeve with adequate internal surface protection works and flanged connections in standard lengths to specified alignment and invert levels. Rates to include for surveying and setting out, stripping top soil, excavation, shoring, disposal of excavated material, backfilling of pipe trenches thereafter and joint sealing of pipes to new manholes along the trench
[8 empty] | 16012.5 | 1.0939
I4 | Steel / Ferrous Pipe Sleeves
[7 empty] | excavation | 7% |  | Add 10%
4.1-I421 | 300mm dia Steel Pipe, not in trench | m |  | 12707 |  |  |  | pipe only
4.1-I422 | 300mm dia Steel Pipe in trenches, depth n.e. 1.5m | m |  | 12969 |  | 400mm dia | 262.5 | 17253.75 | 17516.25
0.73643
4.1-I431 | 400mm dia Steel Pipe | m |  | 17254 |  | 300mm dia | 262.5 | 12706.25 | 12968.75
4.1-I432 | 400mm dia Steel Pipe in trenches, depth n.e. 1.5m | m |  | 17517
PAGE TOTAL CARRIED TO COLLECTION SHEET | [6 empty] | 0.75
I7 | High Density Polyethylene Pipes - HDPE (Double Wall Corrugated - DWC) | [5 empty] | 15000
5%
| Provide, lay, and joint DWC HDPE (SN8) Socket & Spigot sewers in standard lengths to specified alignment and invert levels. Rates to include for surveying and setting out, stripping top soil, excavation, shoring, disposal of excavated material, backfilling of pipe trenches thereafter and joint sealing of pipes to new manholes along the trench | [6 empty] | 10% |  | Supply Only | Excavate & Lay
[7 empty] | excavation | pipe only
I72 | DWC HDPE Sewer, Nominal Bore: 160mm | [5 empty] | 225 | 493.1667 | 718.1667 | 470.75 | 247.4167
4.1-I722 | 160mm dia DWC HDPE Sewer in trenches, depth n.e. 1.5m | m |  | 719 |  |  | 300 | 493.1667 | 793.1667 | 470.75 | 322.4167
[7 empty] | 375 | 493.1667 | 868.1667 | 470.75 | 397.4167
4.1-I723 | Ditto in trenches, but depth 1.5 - 2m | m |  | 794 |  |  | 250
I72 | DWC HDPE Sewer, Nominal Bore: 200mm | [6 empty] | 10% |  | Add 10%
[7 empty] | excavation | pipe only
4.1-I722 | 200mm dia DWC HDPE Sewer in trenches, depth n.e. 1.5m | m |  | 981 |  |  | 225 | 755.3333 | 980.3333 | 1079 |  | 636.6667 | 1.5408
4.1-I723 | Ditto in trenches, but depth 1.5 - 2m | m |  | 1056 |  |  | 300 | 755.3333 | 1055.3333 | 1161
4.1-I724 | Ditto in trenches, but depth 2 - 2.5m | m |  | 1131 |  |  | 375 | 755.3333 | 1130.3333 | 1244
4.1-I725 | Ditto in trenches, but depth 2.5 - 3m | m |  | 1206 |  |  | 450 | 755.3333 | 1205.3333 | 1326
4.1-I726 | Ditto in trenches, but depth 3 - 3.5m | m |  | 1281 |  |  | 525 | 755.3333 | 1280.3333 | 1409
4.1-I727 | Ditto in trenches, but depth 3.5 - 4m | m |  | 1356 |  |  | 600 | 755.3333 | 1355.3333 | 1491
I73 | DWC HDPE Sewer, Nominal Bore: 300mm | [6 empty] | 10% |  | Add 10%
[7 empty] | excavation | pipe only
4.1-I732 | 300mm dia DWC HDPE Sewer in trenches, depth n.e. 1.5m | m |  | 1920 |  |  | 262.5 | 1657.3333 | 1919.8333 | 2112
4.1-I733 | Ditto in trenches, but depth 1.5 - 2m | m |  | 2008 |  |  | 350 | 1657.3333 | 2007.3333 | 2209
4.1-I734 | Ditto in trenches, but depth 2 - 2.5m | m |  | 2095 |  |  | 437.5 | 1657.3333 | 2094.8333 | 2305
4.1-I735 | Ditto in trenches, but depth 2.5 - 3m | m |  | 2183 |  |  | 525 | 1657.3333 | 2182.3333 | 2401
4.1-I736 | Ditto in trenches, but depth 3 - 3.5m | m |  | 2270 |  |  | 612.5 | 1657.3333 | 2269.8333 | 2497
4.1-I737 | Ditto in trenches, but depth 3.5 - 4m | m |  | 2358 |  |  | 700 | 1657.3333 | 2357.3333 | 2594
CLASS K | PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
K15 | Precast Concrete Manholes
| Provide all materials and construct 1200mm internal diameter Precast Reinforced Concrete Ring Manholes with RC Base and Cover and Pipe Benching to details shown on drawings. Include for supply and installation of Heavy duty triangular polyresin composite manhole frame and cover as well as step irons. Rates to include for excavation, preparation of surfaces, disposal of excavated materials, shoring, inset concrete surround for sealing of rings and backfilling, and provision of box out and sealing for all pipes. |  |  |  |  | Excavation | MH Cover & Frame | Step Irons | RC Rings | Base and Cover RC | Sub-Total | Add 10%
4.1-K151 | Manhole depth n.e 1.5m | nr |  | 54745 |  | 843.75 | 18500 | 1750 | 19229.04 | 14421.78 | 54744.57 | 60220 |  | 27200
4.1-K152 | Manhole depth 1.5 - 2m | nr |  | 59082 |  | 984.375 | 18500 | 2100 | 23074.848 | 14421.78 | 59081.003 | 64990
4.1-K153 | Ditto but depth 2 - 2.5m | nr |  | 66122 |  | 1265.625 | 18500 | 2450 | 29484.528 | 14421.78 | 66121.933 | 72735
4.1-K154 | Ditto but depth 2.5 - 3m | nr |  | 73163 |  | 1546.875 | 18500 | 2800 | 35894.208 | 14421.78 | 73162.863 | 80480
4.1-K155 | Ditto but depth 3.0 - 3.5m | nr |  | 80204 |  | 1828.125 | 18500 | 3150 | 42303.888 | 14421.78 | 80203.793 | 88225
4.1-K156 | Ditto but depth 3.5 - 4m | nr |  | 87245 |  | 2109.375 | 18500 | 3500 | 48713.568 | 14421.78 | 87244.723 | 95970
PAGE TOTAL CARRIED TO COLLECTION SHEET
K16 | Precast Concrete Manholes with Backdrop
Provide all materials and construct 1200mm internal diameter Precast Reinforced Concrete Ring Manholes on sewers with backdrop and RC Base and Cover and Pipe Benching to details shown on drawings. Include for supply and installation of Heavy duty triangular polyresin composite manhole frame and cover as well as step irons. Rates to include for excavation, preparation of surfaces, disposal of excavated materials, shoring, inset concrete surround for sealing of rings and backfilling, and provision of box out and sealing for all pipes.
4.1-K164 | Manholes with depth 2.5 - 3m | nr |  | 83163
4.1-K165 | Ditto but depth 3.0 - 3.5m | nr |  | 90204
4.1-K166 | Ditto but depth 3.5 - 4m | nr |  | 97245 |  |  | 7041
4.1-K167 | Ditto but depth exceeding 4m | nr |  | 112245
K6 | Crossings
K61 | Under-River, Stream or Stormwater Canal Crossings, Width n.e 3m
Pipe nominal bore n.e 300mm
4.1-K611.1 | Excavate for trench in river bed n.e. 3m, preparation of surface, disposal of excavated materials, upholding sides of trench, backfilling and removal of redundant services. | m |  | 500 |  |  | 735
4.1-K611.2 | Transport from Site Store, Install, Test and Commission Pipes on under-river crossing | m |  | 100
4.1-K611.2 | Backfill the trench with Concrete C15/20 surround, include for vibration as directed by the Engineer | m3 |  | 12000
4.1-K611.3 | Backfill the trench with approved selected excavated granular material compacted in layers of 300mm as directed by Engineer | m3 |  | 150
Other Crossings
4.1-K641 | Allow for crossing existing HEDGES, including reinstatement to original state. Nominal bore n.e. 300mm | nr |  | 1200
4.1-K651 | Allow for crossing existing boundary WALLS, including reinstatement to original state. Nominal bore n.e. 600mm | nr |  | 4000
4.1-K661 | Allow for crossing existing FENCES (chain link, barbed wire etc.), including reinstatement to original state. Nominal bore n.e. 600mm | nr |  | 1200
4.1-K671 | Allow for crossing existing SEWER AND DRAINS, and reinstate these after construction of sewer has been completed. Pipe internal diameter n.e. 600mm | nr |  | 1200
4.1-K681.1 | Allow for UNDERGROUND TELEPHONE, POWER AND FIBRE CABLE crossing as may be encountered during construction or as directed by the Engineer (provisional). | nr |  | 3000
4.1-K681.2 | Allow for WATER MAIN CROSSINGS including reinstatement to original state as may be encountered during construction or as directed by the Engineer (provisional). | nr |  | 3000
PAGE TOTAL CARRIED TO COLLECTION SHEET
K7 | Reinstatement
Trenchless Road Crossing
4.1-K732.1 | Provide all equipment and materials, tunnel below road surface in common material (soil/murram) using tunnelling technique (Road C57). The rate to include all preparatory works, any requisite shoring, strutting, installation of pipe and pipe casing, anchoring of the pipe, blanking of tunnel ends with mass concrete / masonry walls upon pipework installation and necessary grouting and reinstatement. Pipe nominal bore n.e. 900mm. All works to be executed in close liaison with relevant road authorities and rates to include facilitation of the same. The Bidder to submit Method Statement with Bid for execution of these Works. | m |  | 99000
4.1-K732.2 | Extra over road crossing item 4.1-K732.1 above for tunnelling in rock, all classes (provisional) | m3 |  | 2500
4.1-K732.3 | Allow for any other Method Related charges the Tenderer feels may be required for the Micro-tunneling Works above. These should be indicated below with pricing of each item
| i) | Item | L.S
| ii) | Item | L.S
4.1-K732.4 | Breaking up, temporary and permanent reinstatement of PAVED (Bitumen, Concrete Block Paving, etc.) road with suitable selected excavated material and 300mm thick well graded stabilized gravel with 3% cement content base, compacted in layers of 150mm thick using an 8-10 tone roller, 150mm deep approved compacted hardcore and Surfacing Course to the original material, including supply and application of approved binder layer for bitumen roads, all to the satisfaction of the Engineer. Contractor to include for road cutting, excavation of compacted hardcore / murram, control of Traffic, diversion signage, controls, safety precautions and any other associated works in his rate. | m |  | 8500
4.1-K732.5 | Breaking up, temporary and permanent reinstatement of MURRAM road with 300mm thick well graded stabilized gravel with 3% cement content base compacted using a 8-10 tone roller to the satisfaction of the Engineer. Nominal bore n.e. 900mm. Contractor to include for road cutting, excavation of compacted hardcore / murram, control of Traffic, diversion signage, controls, safety precautions and any other associated works in his rate. | m |  | 2000
4.1-K742.1 | Breaking up, temporary and permanent reinstatement of all murram FOOTPATHS to the satisfaction of the Engineer. Nominal bore n.e. 900mm | m |  | 500
4.1-K742.2 | Breaking up, temporary and permanent reinstatement of all Paved (Bitumen, Cabrio, Reinforced Concrete, etc.) FOOTPATHS to the satisfaction of the Engineer. Nominal bore n.e. 900mm | m |  | 1000
4.1-K751 | Allow for reinstatement of land along the sewer trench after completion of the Works to the satisfaction of the Engineer. | m |  | 80
K8 | Other Pipeline Ancillaries
4.1-K810 | Allow for temporary diversion of drains or waterways where they might interfere with the construction and reinstatement after construction of sewer has been completed. All waterways to be kept operational during construction. | Item | LS | 200000
PAGE TOTAL CARRIED TO COLLECTION SHEET
4.1-K853 | Provide all materials and connect the new sewer line to the existing Sewer. Contractor to include for all requisite fittings, breaking of existing manholes, dealing with sewage flow, boxing out of manholes/ sealing, etc. all to the satisfaction of the Engineer. Nominal bore n.e 300mm | Nr |  | 15000
CLASS L: SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
( Note: Blasting not allowed for any rock excavation)
L11 | Extras to excavation and backfilling in pipe trenches (Provisional)
4.1-L111.1 | Excavation in rock Class A | m3 |  | 1020
4.1-L111.2 | -Ditto- but rock Class B | m3 |  | 1500
4.1-L111.3 | -Ditto- but rock Class C | m3 |  | 2100
4.1-L117.1 | Allow for excavation of soft material below pipe invert level and backfill with approved C15/20 Mass Concrete, depth n.e 1.0m | m3 |  | 12500
4.1-L117.2 | Allow for excavation of soft material below pipe invert level and backfill with approved C15/20 Plum Concrete (size of plums n.e 150mm and total volume n.e 30%), depth n.e 1m (Provisional) | m3 |  | 8000
4.1-L118 | Allow for excavation of soft material below pipe invert level and backfill with approved hardcore, well compacted in layers of 200mm thickness, depth n.e 1m (Provisional) | m3 |  | 750
Extras to excavation and backfilling in Manholes (Provisional)
4.1-L121.1 | Excavation in rock Class A | m3 |  | 1020
4.1-L121.2 | -Ditto- but rock Class B | m3 |  | 1500
4.1-L121.3 | -Ditto- but rock Class C | m3 |  | 2100
4.1-L127.1 | Allow for excavation of soft material below manhole invert level and backfill with approved C15/20 Mass Concrete, depth n.e 1m | m3 |  | 12500
4.1-L127.2 | Allow for excavation of soft material below manhole invert level and backfill with approved C15/20 Plum Concrete (size of plums n.e 150mm and of total volume of plums n.e 30%), depth n.e 1m | m3 |  | 8000
4.1-L128 | Allow for excavation of soft material below manhole invert level and backfill with approved hardcore, well compacted in layers of 200mm thickness, depth n.e 1m (Provisional) | m3 |  | 750
Bed, Haunches and Surrounds
Pipeline nominal bore n.e. 300mm
4.1-L312 | Graded Aggregate / Sand as per specifications Beds 150 mm thick | m |  | 100
4.1-L322 | Selected excavated granular material surround compacted in 150mm layers to Pipe as per specifications | m |  | 50 |  | 47.13 | 42
4.1-L332 | Imported granular material surround compacted in 150mm layers to Pipe as per specifications | m |  | 100
84
PAGE TOTAL CARRIED TO COLLECTION SHEET
Mass Concrete Class 15/20 in 150mm Thick Beds, Haunches and Surrounds, Pipe Nominal bore n.e 300mm
4.1-L542.1 | Bed and haunch Surround Type B | m |  | 3000 |  |  | 3534.75 | 0.25
4.1-L542.1 | Bed and haunch Surround Type C | m |  | 3400
CLASS X: MISCELLANEOUS WORKS
X4 | Rock Filled Gabion
Slopes Structural Protection Measures (Gabions)
4.1-X410 | Provide all materials and carry out laying of 2m x 1m x 1m approved galvanized rock filled gabions, McCaffery or approved equivalent, laid in stretches with 0.5m overlap and mesh wire diameter 5mm. Include for tying of adjacent gabions with approved wire and 16mm dia anchor rods to suit site conditions. All preparatory works to be included in the rate. | Nr |  | 6500
4.1-X420 | Provide all materials and carry out laying of 0.23 - 0.5m thick gabion mattresses, McCaffery or approved equivalent, mesh wire to be galvanized and of minimum dia 5mm. Include approved hardcore fill, tying of adjacent gabions with approved wire and 16mm dia anchor rods to suit site conditions. | m2 |  | 2150
4.1-X421 | Provide, fill and compact in 200 mm layers imported approved excavated material as backing to gabions as directed by the Engineer. Rate to include compaction tests. | m3 |  | 250
4.1-X422 | Extra over for infilling of Gabions with 50mm layer Mass Concrete Class 15/40 | m3 |  | 10200
Surface Protection Measures
4.1-K622.6 | Provide and carry out hydraulic mulch grass seeding to slopes as specified in the Drawings or as directed by the Engineer | m2 |  | 80
4.1-K622.7 | Provide all materials and maintain approved grass planted in above item until it takes root to the satisfaction of the Engineer | m2 |  | 40
X91 | RIVER CROSSING ON PIERS
Details as per Drawing Provided for Aerial Crossings
X911 | Excavation
Rates to include for all strutting, shuttering, stabilizing excavation and preparation of excavated surfaces to receive permanent work.
Excavate for pier footings and Under-River Crossings, part backfill after construction and remainder, cart away to approved tips or use as fill on site, all as directed by the Engineer. Tips to be identified by the Contractor in liaison with the Local Authority.
4.1-X911.1 | Maximum depth n.e. 1.5m | m3 |  | 250
4.1-X911.2 | Depth Exceeding 1.5m | m3 |  | 350
4.1-X911.3 | E.O. excavation items for excavation in rock Class 'A' (Provisional) - Blasting not permitted | m3 |  | 1020
4.1-X911.4 | -Ditto - but rock Class 'B' (Provisional) - Blasting not permitted | m3 |  | 1500
4.1-X911.5 | -Ditto - but rock Class 'C' (Provisional) - Blasting not permitted | m3 |  | 2100
PAGE TOTAL CARRIED TO COLLECTION SHEET
X912 | Concrete Works
Provide, mix and place concrete as directed
4.1-X912 | Plain concrete Class 15/20 in 75mm blinding layer under pier footings. | m2 |  | 950 |  | 765
X913 | Vibrated, Reinforced Concrete Class 25/20 in:-
4.1-X913.1 | Footings | m3 |  | 14000
4.1-X913.2 | Piers | m3 |  | 14000
4.1-X913.3 | Precast / Inset Channel / Pier Head | m3 |  | 14000
X914 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
4.1-X914.1 | 12mm and under | kg |  | 140
4.1-X914.2 | 16mm and over | kg |  | 140
X915 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified.
(i) Vertical Formwork - Class F1 Finish
4.1-X915.1 | Sides of 300mm footings | m2 |  | 700
4.1-X915.2 | Sides of piers in foundations | m2 |  | 700
(ii) Vertical Formwork - Class F2 Finish
4.1-X915.3 | Outer faces of column piers - width 1.0m - 3.0m | m2 |  | 700
X916 | Metal Works
G.M.S Clamps
4.1-X9160 | Provide all material, fabricate and fix 75mm x 6mm thick G.M.S clamp on Steel Pipe Sleeve dia n.e 400mm as detailed in Drag No. M455/W-02/SD/04. Rate to include 12mm Dia. Rawle bolts, Ruberoid, anchor plates, rods, bolts, etc., as detailed. | Nr |  | 5000 |  |  | 434.7
X92 | Method Related Charges (Applicable to River, Stream and Storm Water Drain Crossings)
4.1-X921 | Allow for Diversion Works, including construction of cofferdam etc., for river/ stream/ storm water drain crossing works and reinstate after construction. The River / Waterway to be kept operational during construction. Bidder to submit method statement with Bid for execution of these works. | Item | L.S | 200000
4.1-X922 | Method related charges for keeping excavation free of water which may occur through ground water seepage, rain or other means. | Item | L.S | 200000
PAGE TOTAL CARRIED TO COLLECTION SHEET
4.1-X923 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
X93 | Miscellaneous Works (Provisional)
4.1-X931 | Provisional Sum for other Miscellaneous Works that may be required on site to be carried out as directed by the Engineer. | Item | P.S | 500000
4.1-X932 | Allow a Provisional Sum of Kshs. 1,000,000 to be expended by the Engineer for liaison, facilitation with local residents / community and relevant authorities for access to construction sites, accidental damage, temporary access to working spaces during execution of the works, etc. | Item | P.S | 400000
4.1-X933 | Provisional Sum for carrying out Detailed Topographical Survey for purposes of preparation of construction drawings as directed by the Engineer. | Item | P.S | 400000 |  | 450000
4.1-X934 | Exhaust and demolish existing Septic Tanks along the sewer line alignment. The foul water to be disposed in approved existing designated discharge points within the existing sewerage network, identified by the Contractor in liaison with and approved by Nairobi City Water and Sewerage Company Ltd, and approved by the Engineer. Rate to include for provision of temporary storage of septic water from house holds served by the demolished septic tanks before the sewer connection is completed (Provisional) | nr |  | 13500
4.1-X935 | Provide all requisite materials, pipes, fittings, etc. for realignment of Existing Water Supply Pipes, diameter n.e 300mm. The rate to include for exposing of the Existing Pipes, excavation, laying, jointing, testing, etc. | m |  | 500
4.1-X936 | Provide all requisite materials, pipes, fittings, etc. for realignment of Existing Sewer Pipes, diameter n.e 300mm. The rate to include for exposing of the Existing Pipes, excavation, laying, jointing, testing, etc. | m |  | 700
PAGE TOTAL CARRIED TO COLLECTION SHEET